## Tabelle1
KNX - group objects
for Pichler PKOM4
Modbus |  |  | KNX (default Gateway Adresse 1.1.235)
name | register | adress | adress | name | description | data type | access
FW-Version V9809 |  |  | 13/5/0 | Alarm_Gateway (Modbus-KNX) | status: 0=no alarm _ 1=alarm | DPST-1-5 | R
RaumTemp | 3x | 19 | 13/5/1 | Act. Room Temperature | temperature (-30 - 130 °C) | DPST-9-1 | R
LuftmengeZUL | 3x | 22 | 13/5/2 | Air flow SUP | air flow (m³/h) | DPST-7-1 | R
LuftmengeABL | 3x | 23 | 13/5/3 | Air flow ETA | air flow (m³/h) | DPST-7-1 | R
PowerBW | 3x | 24 | 13/5/4 | Electr. Power DHW Comp. | power (W) | DPST-7-1 | R
PowerHK | 3x | 25 | 13/5/5 | Electr. Power HC Comp. | power (W) | DPST-7-1 | R
PowerPCB_Vent | 3x | 26 | 13/5/6 | Electr. Power PCB+Fans | power (W) | DPST-7-1 | R
KuhlenKwh12M | 3x | 27 | 13/5/7 | Cooling | energy consumption (kWh) | DPST-7-1 | R
LuftungKwh12M | 3x | 29 | 13/5/8 | Ventilation | energy consumption (kWh) | DPST-7-1 | R
BwSnellHeizRestZeit | 3x | 30 | 13/5/9 | Booster E-heater remaining time | time (1 - 65000 min.) _ 0=inactive | DPST-7-6 | R
ErrorStatus4 | 3x | 34 | 13/5/10 | Error | status: 0=no alarm _ 1=alarm | DPST-1-5 | R
Heizleistung | 3x | 37 | 13/5/11 | Heating Capacity | heating power (W) | DPST-8-1 | R
BW_Kwh12M | 3x | 38 | 13/5/12 | DHW | energy consumption (kWh) | DPST-7-1 | R
SCOP12M_Wp_var | 3x | 44 | 13/5/13 | SCOP[12M] Heatpump | SCOP | DPT-9 | R
COP_Akt | 3x | 45 | 13/5/14 | COP [actual] | COP | DPT-9 | R
PVinput | 3x | 62 | 13/5/15 | Pvinput | status: 0=on _ 1=off | DPST-1-1 | R
HeizenKwh12M | 3x | 64 | 13/5/16 | Heating | energy consumption (kWh) | DPST-7-1 | R
TotalKwh12M | 3x | 65 | 13/5/17 | Energy Consumption | energy consumption (kWh) | DPST-7-1 | R
TempZuluft | 3x | 151 | 13/5/18 | T1 Supply Air | temperature (-30 - 130 °C) | DPST-9-1 | R
TempFrischluft | 3x | 152 | 13/5/19 | T3 Outdoor Air | temperature (-30 - 130 °C) | DPST-9-1 | R
TempFortluft | 3x | 153 | 13/5/20 | T4 Exhaust Air | temperature (-30 - 130 °C) | DPST-9-1 | R
TempAbluft | 3x | 156 | 13/5/21 | T7 Extract Air | temperature (-30 - 130 °C) | DPST-9-1 | R
T_SolarFussboden | 3x | 158 | 13/5/22 | T9 Duct heater/solar collector | temperature (-30 - 130 °C) | DPST-9-1 | R
TempBehaelterMitte | 3x | 162 | 13/5/23 | T20 DHW Tank bottom | temperature (-30 - 130 °C) | DPST-9-1 | R
TempBehaelterUnten | 3x | 163 | 13/5/24 | T21 DHW Tank center | temperature (-30 - 130 °C) | DPST-9-1 | R
WpAktLeistungHK | 3x | 186 | 13/5/25 | Act. capacity compressor HC | output (0 - 100 %) | DPST-5-4 | R
ZustandLuft | 3x | 189 | 13/5/26 | Status system | status system according operating manual | DPST-5-10 | R
AktZuluftStufe | 3x | 191 | 13/5/27 | Act. ventilation level SUP | ventilation level: 0=automatic _ 1=level 1 _ 2=level 2 _ 3=level 3 _ 4=level 4 | DPST-5-10 | R
SollRaumTemp | 3x | 193 | 13/5/28 | Setpoint Room temp. | temperature (-30 - 130 °C) | DPST-9-1 | R
AktAbluftStufe | 3x | 194 | 13/5/29 | Status fan ETA | ventilation level: 0=automatic _ 1=level 1 _ 2=level 2 _ 3=level 3 _ 4=level 4 | DPST-5-10 | R
Soll_BW_Wassertemp | 3x | 196 | 13/5/30 | Setpoint DHW | temperature (-30 - 130 °C) | DPST-9-1 | R
BypassZustand | 3x | 205 | 13/5/31 | Status bypass | status: 0=on _ 1=off | DPST-1-1 | R
TempReserve | 3x | 240 | 13/5/32 | T40 Sensor external | temperature (-30 - 130 °C) | DPST-9-1 | R
AktCO2 | 3x | 483 | 13/5/33 | CO2 concentration | CO2 (0 - 10000 ppm) | DPST-7-1 | R
AktRF | 3x | 484 | 13/5/34 | Relative humitidy | humidity (0 - 100%) | DPST-9-7 | R
PumpeExternProzent | 3x | 487 | 13/5/35 | External Pump | output (0 - 100 %) | DPST-5-4 | R
Betriebsart | 4x | 0 | 13/5/36 | Operating mode | operating mode: 0=offf _ 1=summer _ 2=winter _ 3=auto _ 4=vacation _ 5=DHW | DPST-5-10 | R/W
KuhlFreigabe | 4x | 9 | 13/5/37 | Active cooling | release: 0=disabled _ 1=enabled | DPST-1-3 | R/W
SollRaumNormal | 4x | 10 | 13/5/38 | Setpoint room normal | temperature (10 - 30 °C) | DPST-9-1 | R/W
SollRaumAC | 4x | 19 | 13/5/39 | Setpoint room active cooling | temperature (15 - 40 °C) | DPST-9-1 | R/W
ZuluftEinstellungLF1 | 4x | 41 | 13/5/40 | SUP setting ventilation level 1 [reduced level] | air flow (m³/h) | DPST-7-1 | R/W
ZuluftEinstellungLF2 | 4x | 42 | 13/5/41 | SUP setting ventilation level 2 [normal level] | air flow (m³/h) | DPST-7-1 | R/W
ZuluftEinstellungLF3 | 4x | 43 | 13/5/42 | SUP setting ventilation level 3 [heating] | air flow (m³/h) | DPST-7-1 | R/W
ZuluftEinstellungLF4 | 4x | 44 | 13/5/43 | SUP setting ventilation level 4 [intensive _ cooling] | air flow (m³/h) | DPST-7-1 | R/W
LuftstufeGewaelt | 4x | 46 | 13/5/44 | Selected ventilation level | ventilation level: 0=automatic _ 1=level 1 _ 2=level 2 _ 3=level 3 _ 4=level 4 | DPST-5-10 | R/W
CO2SchwelleLS4 | 4x | 101 | 13/5/45 | CO2 concentration to high [increasing of air volume to max. ventilation level 4] | CO2 (0 - 10000 ppm) | DPST-7-1 | R/W
RF_SchwelleLS4 | 4x | 102 | 13/5/46 | Relative humidity to high [increasing of air volume to max. ventilation level 4] | humidity (0 - 100%) | DPST-9-7 | R/W
RF_SchwelleLS2 | 4x | 103 | 13/5/47 | Relative humidity to low [decreasing ventilation level t the next ventilation level] | humidity (0 - 100%) | DPST-9-7 | R/W
BW_Temp | 4x | 129 | 13/5/48 | Setpoint DHW | temperature (-100 - 100 °C) | DPST-9-1 | R/W
E_HeizFreigabe | 4x | 136 | 13/5/49 | E-heater DHW | release: 0=disabled _ 1=enabled | DPST-1-3 | R/W
BW_RaumHeizkreisSollTemp | 4x | 151 | 13/5/50 | Setpoint room temp. heating circuit [T40] | temperature (10 - 30 °C) | DPST-9-1 | R/W
ResetStoerung | 4x | 202 | 13/5/51 | Reset errors | reset aktive alarms | DPST-1-15 | W
FreigabeBW | 4x | 451 | 13/5/52 | DHW | release: 0=disabled _ 1=enabled _ 2=timer | DPST-5-10 | R/W
FreigabeHeizkreis | 4x | 456 | 13/5/53 | Heating circuit | release: 0=disabled _ 1=enabled _ 2=timer | DPST-5-10 | R/W
V2.1 Stand: 10/2019_RRU
MODBUS communication settings
Modbus RTU / Modbus SLAVE
Baud rate = 19200
Parity = Even
Device ID = 41